## 1
Connector type | Fibre type | PC or APC ferrule end face | Attenuation and return loss grades | Visual connector end face requirements | Connector end face geometric and ferrule parameters | Reference connector attenuation requirements | Reference connector end face geometric and ferrule parameters
LC | Single-mode | PC | IEC 61755-2-1 | IEC 61755-2-1 | IEC 61755-3-1 | IEC 61755-2-4 | IEC 61755-3-yy *p
LC | Single-mode | APC | IEC 61755-2-2 | IEC 61755-2-2 | IEC 61755-3-2 | IEC 61755-2-5 | IEC 61755-3-yy *p
LC | Multimode | PC | IEC 63267-2-1 | IEC 63267-2-1 | IEC 63267-3-1 *d | IEC 63267-2-2 | IEC 63267-3-61
LSH | Single-mode | PC | IEC 61755-2-1 | IEC 61755-2-1 | IEC 61755-3-1 | IEC 61755-2-4 | IEC 61755-3-yy *p
LSH | Single-mode | APC | IEC 61755-2-2 | IEC 61755-2-2 | IEC 61755-3-2 | IEC 61755-2-5 | IEC 61755-3-yy *p
LSH | Multimode | PC | IEC 63267-2-1 | IEC 63267-2-1 | IEC 63267-3-1 *d | IEC 63267-2-2 | IEC 63267-3-61
MDC | Single-mode | PC | IEC 61755-2-1 | IEC 61755-2-1 | IEC 61755-3-1 | IEC 61755-2-4 | IEC 61755-3-yy *p
MDC | Single-mode | APC | IEC 61755-2-2 | IEC 61755-2-2 | IEC 61755-3-2 | IEC 61755-2-5 | IEC 61755-3-yy *p
MDC | Multimode | PC | IEC 63267-2-1 | IEC 63267-2-1 | IEC 63267-3-1 *d | IEC 63267-2-2 | IEC 63267-3-61
MPO 1x12 | Single-mode | APC | IEC 61755-2-2 | IEC 61755-2-2 | IEC 61755-3-31 | IEC 61755-2-5 | IEC 61755-3-81 *d
MPO 1x12 | Multimode | PC | IEC 63267-2-1 | IEC 63267-2-1 | IEC PAS 63267-3-31 | IEC 63267-2-2 | IEC 63267-3-81
MPO 1x16 | Single-mode | APC | IEC 61755-2-2 | IEC 61755-2-2 | Not available | IEC 61755-2-5 | Not available
MPO 1x16 | Multimode | PC | IEC 63267-2-1 | IEC 63267-2-1 | Not available | IEC 63267-2-2 | IEC 63267-3-82 *d
MPO 1x16 | Multimode | APC | Not available | Not available | IEC PAS 63267-3-30 | IEC 63267-2-2 | IEC 63267-3-yy *p
MPO 2x12 | Single-mode | APC | IEC 61755-2-2 | IEC 61755-2-2 | Not available | IEC 61755-2-5 | IEC 61755-3-yy *p
MPO 2x12 | Multimode | PC | IEC 63267-2-1 | IEC 63267-2-1 | Not available | IEC 63267-2-2 | Not available
MPO 2x16 | Single-mode | APC | IEC 61755-2-2 | IEC 61755-2-2 | Not available | IEC 61755-2-5 | Not available
MPO 2x16 | Multimode | PC | IEC 63267-2-1 | IEC 63267-2-1 | Not available | IEC 63267-2-2 | Not available
SAC | Single-mode | PC | IEC 61755-2-1 | IEC 61755-2-1 | IEC 61755-3-1 | IEC 61755-2-4 | IEC 61755-3-yy *p
SAC | Single-mode | APC | IEC 61755-2-2 | IEC 61755-2-2 | IEC 61755-3-2 | IEC 61755-2-5 | IEC 61755-3-yy *p
SAC | Multimode | PC | IEC 63267-2-1 | IEC 63267-2-1 | IEC 63267-3-1 *d | IEC 63267-2-2 | IEC 63267-3-61
SC | Single-mode | PC | IEC 61755-2-1 | IEC 61755-2-1 | IEC 61755-3-1 | IEC 61755-2-4 | IEC 61755-3-yy *p
SC | Single-mode | APC | IEC 61755-2-2 | IEC 61755-2-2 | IEC 61755-3-2 | IEC 61755-2-5 | IEC 61755-3-yy *p
SC | Multimode | PC | IEC 63267-2-1 | IEC 63267-2-1 | IEC 63267-3-1 *d | IEC 63267-2-2 | IEC 63267-3-61
SEN | Single-mode | PC | IEC 61755-2-1 | IEC 61755-2-1 | IEC 61755-3-1 | IEC 61755-2-4 | IEC 61755-3-yy *p
SEN | Single-mode | APC | IEC 61755-2-2 | IEC 61755-2-2 | IEC 61755-3-2 | IEC 61755-2-5 | IEC 61755-3-yy *p
SEN | Multimode | PC | IEC 63267-2-1 | IEC 63267-2-1 | IEC 63267-3-1 *d | IEC 63267-2-2 | IEC 63267-3-61

## 2
Connector type | Mechanical connector interface
LC | IEC 61754-20
LSH | IEC 61754-15
MDC | IEC 61754-37
MPO 1x12 | IEC 61754-7-1
MPO 1x16 | IEC 61754-7-4 *d
MPO 2x12 | IEC 61754-7-2
MPO 2x16 | IEC 61754-7-3
SAC | IEC 61754-36
SC | IEC 61754-4
SEN | IEC 61754-38 *d

## 3
Performance category - operating service environment (temperature range) | Fibre type | Mechanical and environmental connector performance (terminated as pigtail or patchcord)
C | Single-mode | IEC 61753-021-02
C | Multimode | IEC 61753-022-2
C-HD | Single-mode | IEC 61753-1, category C-HD
C-HD | Multimode | IEC 61753-1, category C-HD
OP | Single-mode | IEC 61753-021-03 *d
OP | Multimode | IEC 61753-1, category OP
OP-HD | Single-mode | IEC 61753-1, category OP-HD
OP-HD | Multimode | IEC 61753-1, category OP-HD
OP+ | Single-mode | IEC 61753-021-06
OP+ | Multimode | IEC 61753-1, category OP+
OP+-HD | Single-mode | IEC 61753-1, category OP+HD
OP+-HD | Multimode | IEC 61753-022-13 *d

## 4
Cable type | Connector type | Mechanical and environmental cable performance (terminated as cable assembly)
Primary coated fibre | LC | According to fibre specification
Primary coated fibre | LSH | According to fibre specification
Primary coated fibre | MDC | According to fibre specification
Primary coated fibre | MPO 1x12 | According to fibre specification
Primary coated fibre | MPO 1x16 | According to fibre specification
Primary coated fibre | MPO 2x12 | According to fibre specification
Primary coated fibre | MPO 2x16 | According to fibre specification
Primary coated fibre | SAC | According to fibre specification
Primary coated fibre | SC | According to fibre specification
Primary coated fibre | SEN | According to fibre specification
Buffered fibre | LC | IEC 60794-1-32 *d
Buffered fibre | LSH | IEC 60794-1-32 *d
Buffered fibre | MDC | IEC 60794-1-32 *d
Buffered fibre | MPO 1x12 | Not available
Buffered fibre | MPO 1x16 | Not available
Buffered fibre | MPO 2x12 | Not available
Buffered fibre | MPO 2x16 | Not available
Buffered fibre | SAC | IEC 60794-1-32 *d
Buffered fibre | SC | IEC 60794-1-32 *d
Buffered fibre | SEN | IEC 60794-1-32 *d
Ribbon fibre | LC | Not available
Ribbon fibre | LSH | Not available
Ribbon fibre | MDC | Not available
Ribbon fibre | MPO 1x12 | IEC 60794-1-31
Ribbon fibre | MPO 1x16 | IEC 60794-1-31
Ribbon fibre | MPO 2x12 | IEC 60794-1-31
Ribbon fibre | MPO 2x16 | IEC 60794-1-31
Ribbon fibre | SAC | Not available
Ribbon fibre | SC | Not available
Ribbon fibre | SEN | Not available
Reinforced cable | LC | IEC 60794-2-50 for performance categories C, C-HD, OP and OP-HD
Reinforced cable | LSH | IEC 60794-2-50 for performance categories C, C-HD, OP and OP-HD
Reinforced cable | MDC | IEC 60794-2-50 for performance categories C, C-HD, OP and OP-HD
Reinforced cable | MPO 1x12 | IEC 60794-2-23 for performance categories C, C-HD, OP and OP-HD
Reinforced cable | MPO 1x16 | IEC 60794-2-23 for performance categories C, C-HD, OP and OP-HD
Reinforced cable | MPO 2x12 | IEC 60794-2-23 for performance categories C, C-HD, OP and OP-HD
Reinforced cable | MPO 2x16 | IEC 60794-2-23 for performance categories C, C-HD, OP and OP-HD
Reinforced cable | SAC | IEC 60794-2-50 for performance categories C, C-HD, OP and OP-HD
Reinforced cable | SC | IEC 60794-2-50 for performance categories C, C-HD, OP and OP-HD
Reinforced cable | SEN | IEC 60794-2-50 for performance categories C, C-HD, OP and OP-HD

## 5
Connector type | Attenuation measurement of randomly mated connectors
LC | IEC 61300-3-34
LSH | IEC 61300-3-34
MDC | IEC 61300-3-34
MPO 1x12 | IEC 61300-3-45
MPO 1x16 | IEC 61300-3-45
MPO 2x12 | IEC 61300-3-45
MPO 2x16 | IEC 61300-3-45
SAC | IEC 61300-3-34
SC | IEC 61300-3-34
SEN | IEC 61300-3-34

## 6
Connector type | Fibre type | Attenuation and return loss measurement of installed cable plant
LC | Single-mode | IEC 61280-4-2
LC | Multimode | IEC 61280-4-1
LSH | Single-mode | IEC 61280-4-2
LSH | Multimode | IEC 61280-4-1
MDC | Single-mode | IEC 61280-4-2
MDC | Multimode | IEC 61280-4-1
MPO 1x12 | Single-mode | IEC 61280-4-5
MPO 1x12 | Multimode | IEC 61280-4-5
MPO 1x16 | Single-mode | IEC 61280-4-5
MPO 1x16 | Multimode | IEC 61280-4-5
MPO 2x12 | Single-mode | IEC 61280-4-5
MPO 2x12 | Multimode | IEC 61280-4-5
MPO 2x16 | Single-mode | IEC 61280-4-5
MPO 2x16 | Multimode | IEC 61280-4-5
SAC | Single-mode | IEC 61280-4-2
SAC | Multimode | IEC 61280-4-1
SC | Single-mode | IEC 61280-4-2
SC | Multimode | IEC 61280-4-1
SEN | Single-mode | IEC 61280-4-2
SEN | Multimode | IEC 61280-4-1

## 7
Fibre type | Standard
Single-mode | IEC 60793-2-50
Multimode | IEC 60793-2-10

## 8
Standard | Scope
IEC 61300-3-4 | Attenuation measurement against reference
IEC 61300-3-6 | Return loss measurement
IEC 61300-3-35 | Visual connector end face inspection procedure
IEC 61300-3-35 | Visual connector end face inspection microscope requirements
ISO/IEC 14763-2 | Planning and installation of premises cabling
ISO/IEC 14763-3 | Testing of optical fibre cabling (inspection and cleaning of connector end faces, optical performance testing)
IEC TR 62627-01 | Cleaning methods

## A
Connector type | Single-mode | Multimode | Single-mode, Ferrule end face, PC | Single-mode, Ferrule end face, APC | Multimode, Ferrule end face, PC | Multimode, Ferrule end face, APC
LC | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE
LSH | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE
MDC | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE
MPO 1x12 | TRUE | TRUE | FALSE | TRUE | TRUE | FALSE
MPO 1x16 | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE
MPO 2x12 | TRUE | TRUE | FALSE | TRUE | TRUE | FALSE
MPO 2x16 | TRUE | TRUE | FALSE | TRUE | TRUE | FALSE
SAC | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE
SC | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE
SEN | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE

## B
Attenuation grade | Single-mode | Multimode
B (mean ≤ 0,12 dB; at least 97 % ≤ 0,25 dB) | TRUE | FALSE
C (mean ≤ 0,25 dB; at least 97 % ≤ 0,5 dB) | TRUE | FALSE
D (mean ≤ 0,5 dB; at least 97% ≤ 1,0 dB) | TRUE | FALSE
Bm (mean ≤ 0,3 dB; at least 97 % ≤ 0,6 dB) | FALSE | TRUE
Cm (mean ≤ 0,5 dB; at least 97 % ≤ 1,0 dB) | FALSE | TRUE

## C
Return loss grade | Single-mode | Multimode | PC | APC
1 (≥ 60 dB, mated) | TRUE | FALSE | FALSE | TRUE
2 (≥ 45 dB, mated) | TRUE | FALSE | TRUE | FALSE
3 (≥ 35 dB, mated) | TRUE | FALSE | TRUE | FALSE
4 (≥ 26 dB, mated) | TRUE | FALSE | TRUE | FALSE
1m (≥ 45 dB, mated) | FALSE | TRUE | FALSE | TRUE
2m (≥ 20 dB, mated) | FALSE | TRUE | TRUE | FALSE

## D
Connector type | Primary coated fibre | Buffered fibre | Ribbon fibre | Reinforced cable
LC | TRUE | TRUE | FALSE | TRUE
LSH | TRUE | TRUE | FALSE | TRUE
MDC | TRUE | TRUE | FALSE | TRUE
MPO 1x12 | TRUE | FALSE | TRUE | TRUE
MPO 1x16 | TRUE | FALSE | TRUE | TRUE
MPO 2x12 | TRUE | FALSE | TRUE | TRUE
MPO 2x16 | TRUE | FALSE | TRUE | TRUE
SAC | TRUE | TRUE | FALSE | TRUE
SC | TRUE | TRUE | FALSE | TRUE
SEN | TRUE | TRUE | FALSE | TRUE

## Filter 1
IN1 | IN2 | IN4
LC | Single-mode | PC
LC | Single-mode | APC
LC | Multimode | PC
LSH | Single-mode | PC
LSH | Single-mode | APC
LSH | Multimode | PC
MDC | Single-mode | PC
MDC | Single-mode | APC
MDC | Multimode | PC
MPO 1x12 | Single-mode | APC
MPO 1x12 | Multimode | PC
MPO 1x16 | Single-mode | APC
MPO 1x16 | Multimode | PC
MPO 1x16 | Multimode | APC
MPO 2x12 | Single-mode | APC
MPO 2x12 | Multimode | PC
MPO 2x16 | Single-mode | APC
MPO 2x16 | Multimode | PC
SAC | Single-mode | PC
SAC | Single-mode | APC
SAC | Multimode | PC
SC | Single-mode | PC
SC | Single-mode | APC
SC | Multimode | PC
SEN | Single-mode | PC
SEN | Single-mode | APC
SEN | Multimode | PC

## Filter 2
IN2 | IN4 | IN6
Single-mode | APC | 1 (≥ 60 dB, mated)
Single-mode | PC | 2 (≥ 45 dB, mated)
Single-mode | PC | 3 (≥ 35 dB, mated)
Single-mode | PC | 4 (≥ 26 dB, mated)
Multimode | APC | 1m (≥ 45 dB, mated)
Multimode | PC | 2m (≥ 20 dB, mated)

## Filter 3
IN5 | IN2
B (mean ≤ 0,12 dB; at least 97 % ≤ 0,25 dB) | Single-mode
C (mean ≤ 0,25 dB; at least 97 % ≤ 0,5 dB) | Single-mode
D (mean ≤ 0,5 dB; at least 97% ≤ 1,0 dB) | Single-mode
Bm (mean ≤ 0,3 dB; at least 97 % ≤ 0,6 dB) | Multimode
Cm (mean ≤ 0,5 dB; at least 97 % ≤ 1,0 dB) | Multimode

## Filter 4
IN3 | IN1
Primary coated fibre | LC
Primary coated fibre | LSH
Primary coated fibre | MDC
Primary coated fibre | MPO 1x12
Primary coated fibre | MPO 1x16
Primary coated fibre | MPO 2x12
Primary coated fibre | MPO 2x16
Primary coated fibre | SAC
Primary coated fibre | SC
Primary coated fibre | SEN
Buffered fibre | LC
Buffered fibre | LSH
Buffered fibre | MDC
Buffered fibre | MPO 1x12
Buffered fibre | MPO 1x16
Buffered fibre | MPO 2x12
Buffered fibre | MPO 2x16
Buffered fibre | SAC
Buffered fibre | SC
Buffered fibre | SEN
Ribbon fibre | LC
Ribbon fibre | LSH
Ribbon fibre | MDC
Ribbon fibre | MPO 1x12
Ribbon fibre | MPO 1x16
Ribbon fibre | MPO 2x12
Ribbon fibre | MPO 2x16
Ribbon fibre | SAC
Ribbon fibre | SC
Ribbon fibre | SEN
Reinforced cable | LC
Reinforced cable | LSH
Reinforced cable | MDC
Reinforced cable | MPO 1x12
Reinforced cable | MPO 1x16
Reinforced cable | MPO 2x12
Reinforced cable | MPO 2x16
Reinforced cable | SAC
Reinforced cable | SC
Reinforced cable | SEN